## Slide 1: Reservoirs
Workshop for Water Sector Team
08/10/2018 to 12/10/2018

## Slide 2: Design process
Assess the area
→ Identification of best network coverage (chapter3)
Sketch the design
→ Chapter 4
Choice of a type of network and repartition
→ Chapter 5
Calculate the theoretical repartition of the flow
→ Chapter 6
Calculate the real DB repartition
→ Distribution Box repartition
Calculate the reservoir volume
→ Reservoir size calculation
Caclulate the pipeline diameter
→ Pipeline design

## Slide 3: Reservoirs
Store water when faucet of WP is closed
Night storage
  Useless to calculate storage for more than 14 h

## Slide 4: New Approach Construction of one Reservoir for one WP
Advantage | Disadvantage
Common reservoir | 
Sharing the volume above the partition | On steep slope to much pressure on faucets
On spot | 
Each community manage its storage Easier to understand Overflow goes to cattle trough Quick and easy to build with mould | No sharing the volume above the partition

## Slide 5: Reservoir is close to WP If possible above

## Slide 6: Reservoir overflow to cattle through

## Slide 7: Concrete Reservoir construction Extremely durable
Foundation
Slab reinforcement
Slab
Placing inside mould
Vertical reinforcement
Circular reinforcement
Casting the wall
Wall finished
Reservoir finished

## Slide 8: Total daily needs
Amount of water required to supply the population of the WP:

## Slide 9: Daily production
Theoretical flow (in dry season) that will supply the reservoir in one day:
The inlet yield is the flow that is coming out of the DB to supply the community (see DB design)
  x 24 (hr/day)

## Slide 10: Daytime production
Theoretical flow (in dry season) that will supply the reservoir during the 10 h of the day:
The inlet yield is the flow that is coming out of the DB to supply the community (see DB design)
x 10 (hr/daytime)

## Slide 11: Designer choices
Possible case |  | Designer choices
A | Needs < Daytime production | Open Flow
B | Needs > Daytime production and Needs < Daily production | Reservoir
C | Needs > Daily production | Needs are not covered → Ask your coordinator for help on this design

## Slide 12: Example: Bisha network
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) |  |  |  | 
② | Inlet flow_ Dry season (l/s) |  |  |  | 
③ | Daily prod (l/day) |  |  |  | 
④ | Daytime prod (l/day) |  |  |  | 
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 

## Slide 13: ① Calculate the total needs for each WP
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) |  |  |  | 
② | Inlet flow_ Dry season (l/s) |  |  |  | 
③ | Daily prod (l/day) |  |  |  | 
④ | Daytime prod (l/day) |  |  |  | 
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 

## Slide 14: ① Calculate the total needs for each WP
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) |  |  |  | 
③ | Daily prod (l/day) |  |  |  | 
④ | Daytime prod (l/day) |  |  |  | 
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 

## Slide 15: ② Take the inlet flow from DB calculation
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) |  |  |  | 
③ | Daily prod (l/day) |  |  |  | 
④ | Daytime prod (l/day) |  |  |  | 
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 

## Slide 16: ② Take the inlet flow from DB calculation
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) | 0.125 l/s | 0.125 l/s | 0.1 l/s | 0.04 l/s
③ | Daily prod (l/day) |  |  |  | 
④ | Daytime prod (l/day) |  |  |  | 
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 

## Slide 17: ③ Calculate the Daily Production
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) | 0.125 l/s | 0.125 l/s | 0.1 l/s | 0.04 l/s
③ | Daily prod (l/day) |  |  |  | 
④ | Daytime prod (l/day) |  |  |  | 
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 
X 86400

## Slide 18: ③ Calculate the Daily Production
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) | 0.125 l/s | 0.125 l/s | 0.1 l/s | 0.04 l/s
③ | Daily prod (l/day) | 10800 l | 10800 l | 8640 l | 3456 l
④ | Daytime prod (l/day) |  |  |  | 
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 
X 86400
There is enough inlet flow to supply the needs.

## Slide 19: ④ Calculate the Daytime Production
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) | 0.125 l/s | 0.125 l/s | 0.1 l/s | 0.04 l/s
③ | Daily prod (l/day) | 10800 l | 10800 l | 8640 l | 3456 l
④ | Daytime prod (l/day) |  |  |  | 
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 
X 36000

## Slide 20: ④ Calculate the Daytime Production
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) | 0.125 l/s | 0.125 l/s | 0.1 l/s | 0.04 l/s
③ | Daily prod (l/day) | 10800 l | 10800 l | 8640 l | 3456 l
④ | Daytime prod (l/day) | 4500 l | 4500 l | 3600 l | 1 440 l
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 
X 36000

## Slide 21: ⑤ Define the type of storage
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) | 0.125 l/s | 0.125 l/s | 0.1 l/s | 0.04 l/s
③ | Daily prod (l/day) | 10800 l | 10800 l | 8640 l | 3456 l
④ | Daytime prod (l/day) | 4500 l | 4500 l | 3600 l | 1 440 l
⑤ | Type of storage |  |  |  | 
⑥ | V reservoir calculated (l) |  |  |  | 
If ① < ④ (Total Need < Daytime production)  Open flow
If ① > ④ (Total Need > Daytime production)  Night storage
The water needs to be stored at night.

## Slide 22: ⑤ Calculate the Volume of the reservoir
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) | 0.125 l/s | 0.125 l/s | 0.1 l/s | 0.04 l/s
③ | Daily prod (l/day) | 10800 l | 10800 l | 8640 l | 3456 l
④ | Daytime prod (l/day) | 4500 l | 4500 l | 3600 l | 1 440 l
⑤ | Type of storage | Night storage | Night storage | Night storage | Night storage
⑥ | V reservoir calculated (l) |  |  |  | 

## Slide 23: ⑤ Calculate the Volume of the reservoir
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) | 0.125 l/s | 0.125 l/s | 0.1 l/s | 0.04 l/s
③ | Daily prod (l/day) | 10800 l | 10800 l | 8640 l | 3456 l
④ | Daytime prod (l/day) | 4500 l | 4500 l | 3600 l | 1 440 l
⑤ | Type of storage | Night storage | Night storage | Night storage | Night storage
⑥ | V reservoir calculated (l) | 6300 - 4500 = 1800 l |  |  | 

## Slide 24: ⑤ Calculate the Volume of the reservoir
 | WP name | Masana | Bobichwada | Diblecheba | Bobichwada school
 | Nb of HH | 70 HH | 65 HH | 52 HH | 750 students
① | Total Needs (l/day) | 6300 l | 5850 l | 4680 l | 2250 l
② | Inlet flow_ Dry season (l/s) | 0.125 l/s | 0.125 l/s | 0.1 l/s | 0.04 l/s
③ | Daily prod (l/day) | 10800 l | 10800 l | 8640 l | 3456 l
④ | Daytime prod (l/day) | 4500 l | 4500 l | 3600 l | 1 440 l
⑤ | Type of storage | Night storage | Night storage | Night storage | Night storage
⑥ | V reservoir calculated (l) | 6300 - 4500 = 1800 l | 5850 - 4500 = 1350 l | 4680 – 3600 = 1080 l | 2250 – 1440 = 810 l